## Troubleshooting
BKF D500 KITCEHN HOOD EXHUST FAN
Symptom | No. | Possible Cause | Corrective Action
Fan not operating / does not start | 1 | No power supply, blown fuse, tripped breaker, or isolator switched OFF. | Check incoming supply, isolator, fuse, and breaker. Restore correct power supply only after confirming safe condition.
| 2 | Loose, disconnected, or incorrect electrical wiring. | Isolate power, inspect terminals, tighten connections, and verify wiring as per approved wiring diagram.
| 3 | Motor protection, PTC, thermal overload, or VFD fault is active. | Check protection relay/VFD fault code, reset only after finding the cause. Verify motor current against nameplate.
| 4 | Motor defective or winding damaged. | Test insulation resistance and winding continuity. Repair or replace motor as per Systemair/motor manufacturer recommendation.
| 5 | Impeller blocked by foreign object or mechanical obstruction. | Isolate power, open access safely, remove obstruction, clean fan, and manually check free rotation before restarting.
Wrong rotation / airflow opposite direction | 1 | Three-phase supply phase sequence is incorrect. | Check rotation direction after start-up. Interchange two phases at supply side if rotation is wrong.
| 2 | Incorrect VFD output phase connection. | Verify VFD output wiring and rotation command. Correct phase sequence and retest.
| 3 | Fan installed opposite to intended airflow direction. | Check arrow mark on casing and approved duct airflow direction. Correct installation if fan orientation is wrong.
Insufficient airflow | 1 | Duct system blocked, damper closed, fire/smoke damper closed, or external static pressure higher than design. | Inspect duct route, dampers, louvers, and smoke/fire damper status. Remove blockage and set dampers to approved position.
| 2 | Impeller dirty, grease/dust deposits, or fan casing fouled. | Clean impeller and casing. For kitchen/grease duty, increase cleaning frequency and check filters/grease traps.
| 3 | Fan rotating in wrong direction. | Check actual wheel rotation and correct phase sequence/VFD wiring.
| 4 | VFD frequency set too low or speed control command incorrect. | Check operating frequency and control signal. Adjust within approved range and fan nameplate limits.
| 5 | Flexible connector collapsed, duct leakage, or access door left open. | Inspect ductwork, flexible connections, and access doors. Seal leakage and repair damaged sections.
| 6 | Incorrect fan selection or operating point outside approved performance curve. | Compare measured airflow/static pressure with approved selection. Escalate to design/supplier if fan cannot meet duty.
Excessive noise | 1 | Non-typical bearing noise or defective motor bearing. | Stop fan if noise is abnormal. Check bearing condition and replace motor/bearing through authorized service.
| 2 | Impeller unbalanced due to dirt, grease, or damage. | Clean impeller, check for damage, and balance/replace impeller if vibration remains.
| 3 | Loose mounting bolts, loose casing, or fan not securely anchored. | Tighten anchor bolts, frame, casing screws, and supports. Verify anti-vibration mounts if provided.
| 4 | High air velocity, duct turbulence, or pressure pulsation. | Check duct transitions, bends, dampers, and system resistance. Rectify turbulence and confirm operation within fan curve.
| 5 | VFD/motor electrical noise due to missing sine/dU/dt filter or long cable. | Check VFD installation. Use approved all-pole sine filter or dU/dt filter where required by Systemair/motor instructions.
Excessive vibration | 1 | Impeller imbalance caused by dirt build-up or mechanical damage. | Clean impeller and inspect blades. Balance or replace impeller if vibration exceeds acceptable level.
| 2 | Fan base, frame, or duct connection not rigid / not aligned. | Check supports, base frame, flexible connector, and duct alignment. Re-level and secure installation.
| 3 | Fan operating near unstable point or pressure pulsation due to system condition. | Check airflow, static pressure, damper position, and duct restrictions. Adjust system to stable operating point.
| 4 | Motor bearing or shaft problem. | Check bearing noise, shaft runout, and motor condition. Replace defective motor or bearing assembly.
Motor overheating / high current | 1 | Overcurrent due to fan operating outside nameplate limits or excessive airflow load. | Measure voltage, current, frequency, and static pressure. Adjust operating point within nameplate and approved selection.
| 2 | Overvoltage, undervoltage, phase imbalance, or single phasing. | Check supply voltage and phase balance. Correct electrical supply issue before restarting.
| 3 | Blocked cooling path, dirty motor, or poor ventilation around external motor. | Clean motor cooling fins and ensure well-ventilated installation area. Remove any obstruction around motor.
| 4 | Excessive switching frequency or frequent start/stop operation. | Review control sequence. BKF is intended for continuous operation; avoid extreme switching.
| 5 | VFD parameters incorrect or frequency outside approved operating range. | Check VFD settings, acceleration/deceleration, min/max frequency, motor data, and protection settings.
| 6 | Impeller rubbing or mechanical resistance. | Isolate power, rotate impeller manually, check clearances, remove obstruction, and correct alignment.
VFD fault / drive trip | 1 | Incorrect VFD parameter settings for motor rated current, voltage, frequency, or ramp time. | Enter motor nameplate data correctly and adjust ramp/protection settings as per approved commissioning procedure.
| 2 | Voltage peaks at motor terminals due to long cable or missing output filter. | Install/verify sine filter or dU/dt filter as recommended. Check cable length and earthing.
| 3 | Fan load too high because system resistance/damper condition is incorrect. | Check damper status, duct pressure, and airflow. Remove restrictions and restart after confirming load is normal.
| 4 | Overtemperature or overcurrent alarm generated by motor protection. | Investigate motor temperature/current cause. Do not repeatedly reset without correction.
Pressure pulsation / unstable operation | 1 | Fan operating outside stable area of performance curve. | Measure airflow/static pressure and compare with selection. Adjust dampers or system resistance to approved operating point.
| 2 | Duct design issue: sharp bend, poor transition, or obstruction near fan inlet/outlet. | Inspect duct geometry around fan. Provide proper straight length/transitions or rectify obstruction where possible.
| 3 | Damper too close to fan or partially closed causing turbulence. | Adjust damper position and review location. Keep operation within stable range.
Smoke extraction / emergency mode not functioning | 1 | Motor protective devices, PTC, or VFD not correctly bypassed for fire mode where required by approved sequence. | Verify fire-mode control logic with approved fire strategy. Ensure required bypass/max-speed operation is functional.
| 2 | Fan does not switch to maximum speed after fire signal or after short supply interruption. | Test fire signal, control relay, VFD bypass/contactors, and restart logic. Correct sequence before acceptance.
| 3 | Incorrect temperature/time class or fan identification for smoke duty. | Check nameplate, approval submittal, and fan certification. Do not use fan for smoke extraction if rating is not compliant.
| 4 | Fan installed inside wrong fire zone or not in well-ventilated approved location. | Review installation location against approved drawings and Systemair instructions. Relocate or protect as required.
Foreign object / impeller contact | 1 | Foreign particles entered fan due to missing protection or open duct during construction. | Remove foreign object, inspect impeller/casing damage, clean internal area, and install protection until final operation.
| 2 | Outlet/inlet not protected where access to impeller is possible. | Install approved protective grid/accessory where required and confirm no person can touch rotating parts during operation.
| 3 | Impeller shifted, casing damaged, or clearance lost due to handling/installation impact. | Check casing alignment and impeller clearance. Repair casing or replace damaged components.
Grease/dust deposit build-up | 1 | Kitchen exhaust or dusty air without adequate filtering/cleaning frequency. | Clean fan and ductwork. Confirm application is suitable and improve filtration/grease management where required.
| 2 | Maintenance access not provided or access door not used for periodic cleaning. | Provide safe access, establish cleaning schedule, and record maintenance activity.
| 3 | Fan used for medium with excessive dust/grease beyond intended limits. | Review application suitability. Provide appropriate filtration or consult supplier for correct fan/application.

## Sources
Source / Basis | URL / Note
Systemair BKF rectangular duct fans product page | https://www.systemair.com/en/products/fans/duct-fans/rectangular-duct-fans/bkf
Systemair BKF Installation and Operating Instructions | https://planetaklimata.com.ua/instr/Systemair/Systemair_BKF_Installation_Manual_Eng.pdf
Prepared note | Prepared for Systemair BKF500 D6 site troubleshooting. Verify against project-approved submittal, wiring diagram, VFD settings, fire mode sequence, and local code requirements.