## Checklist
TROUBLESHOOTING CHECKLIST
Symptom | No. | Possible Cause(s) | Corrective Action
Excessive Noise | 1 | Defective or loose motor bearings. | Replace motor with same frame size, RPM, HP.
| 2 | Ventilator base not securely anchored. | Reset properly.
| 3 | Loose or unbalanced wheel/propeller. | Tighten screws, remove build-up, balance wheel/propeller.
| 4 | Misaligned pulleys or shaft. | Correct alignment.
| 5 | Loose or damaged wheel/propeller. | Replace wheel/propeller.
| 6 | Wheel running in wrong direction. | Reverse direction.
Fan Inoperative | 1 | Blown fuse or open circuit breaker. | Replace fuses or circuit breaker.
| 2 | Loose or disconnected wiring. | Shut off power and check wiring for proper connections.
| 3 | Defective motor. | Repair or replace motor.
| 4 | Broken belts. | Replace belts.
Insufficient Airflow | 1 | Open access doors or loose sections of ducts. | Check for leakage.
| 2 | Clogged filters. | Clean filters.
| 3 | Operation in wrong direction. | Correct rotation of wheel.
| 4 | Insufficient make-up air direction. | Add make-up fan or louver opening.
Water Leaking into Ductwork or Collection of Grease Under Fan | 1 | Fan installed with slope in the wrong direction. | Slope should be fitted in the direction of the drainage opening or grease collection box and drain spout.
| 2 | Clogged drain spout. | Clean drain spout.
| 3 | Cooling tube or motor dome top removed. | Install new cooling tube with gasket and dome top.
| 4 | Grease container full. | Empty grease box.
Motor Overheating | 1 | Belt slippage. | Adjust tension or replace belts.
| 2 | Overvoltage or under voltage. | Contact power supply company.
| 3 | Operation in wrong direction. | Reverse direction of motor.
| 4 | Fan speed too high. | Slow down fan by opening variable pitch pulley on motor shaft.
| 5 | Incorrect motor (service factor 1.0, low ambient temp.). | Replace motor with correct open, NEMA service factors (1.15 or higher) with 40 degrees ambient.
| 6 | Blocked cooling tube or leaky gasket. | Remove blockage and seal cooling tube in place.
| 7 | Insufficient airflow to kitchen hood fan operating on low speed with kitchen in full operation. | Check airflow under hood and adjust kitchen equipment output.
| 8 | Undersized motor. | Check motor ratings with catalog speed and air capacity chart.
Note | Care should be taken to follow all local electrical, safety and building codes. Provisions of the National Electric Code (NEC), as well as the Occupational Safety and Health Act (OSHA) should be followed.
Service | All motors are checked prior to shipment. If motor defects should develop, prompt service can be obtained from the nearest authorized service station of the motor manufacturer while under warranty. Exchange, repair or replacement will be provided on a no charge basis if the motor is defective within the warranty period. The YORK® by Johnson Controls representative in your area will provide a name and address of an authorized service station if requested.
Warning | WARNING: Motor guarantee is void unless overload protection is provided in motor wiring circuit.

## Summary
TROUBLESHOOTING CHECKLIST SUMMARY
Symptom | No. of Checks | Typical Area | Priority
Excessive Noise | 6 | Fan assembly / mounting / rotation | Medium
Fan Inoperative | 4 | Electrical / motor / belts | High
Insufficient Airflow | 4 | Duct leakage / filters / rotation / make-up air | High
Water Leaking into Ductwork or Collection of Grease Under Fan | 4 | Slope / drain / grease box | Medium
Motor Overheating | 8 | Power / belts / airflow / motor sizing | High

## Source Notes
Item | Details
Source | Uploaded PDF: Troubleshooting Checklist, page 1
Origin shown | Johnson Controls / YORK
Conversion | PDF page converted into editable Excel checklist.
Added fields | Status and Remarks columns added for site use.
Safety note | Care should be taken to follow all local electrical, safety and building codes. Provisions of the National Electric Code (NEC), as well as the Occupational Safety and Health Act (OSHA) should be followed.
Warning | WARNING: Motor guarantee is void unless overload protection is provided in motor wiring circuit.