## Breakdown Table
HMU TROUBLE SHOOTING & MAINTENANCE
EVERY OPERATION ON THE SYSTEM OR ON THE ELECTRICAL APPLIANCES MUST BE CARRIED OUT ONLY BY A QUALIFIED MAINTENANCE TECHNICIAN.
S.No. | FAULT | COMPONENT | POSSIBLE CAUSE / SOLUTION
1 | EXCESSIVE NOISE | Fan rotator | The rotator is deformed, unbalanced or loose
2 | EXCESSIVE NOISE | Fan rotator | The nozzle is damaged
3 | EXCESSIVE NOISE | Fan rotator | Foreign bodies have entered the fan
4 | EXCESSIVE NOISE | Transmission | Pulley loose on the shaft
5 | EXCESSIVE NOISE | Transmission | Pulley not aligned
6 | EXCESSIVE NOISE | Transmission | Loose, too tight, worn, greasy, dirty or wronglysized belts
7 | EXCESSIVE NOISE | Transmission | Motor or fan not well anchored
8 | EXCESSIVE NOISE | Bearings | No lubrication
9 | EXCESSIVE NOISE | Bearings | Loose bearing supports
10 | EXCESSIVE NOISE | Bearings | Worn or deformed bearings
11 | EXCESSIVE NOISE | Motor | Incorrect supply voltage
12 | EXCESSIVE NOISE | Motor | Worn bearings
13 | EXCESSIVE NOISE | Motor | Contact between rotor and stator
14 | EXCESSIVE NOISE | In the channels | Excessive speed in the channels
15 | EXCESSIVE NOISE | In the channels | Too tight anti-vibration joint
16 | INSUFFICIENT AIR FLOW | Fan | Wrong rotation direction
17 | INSUFFICIENT AIR FLOW | Channels | Greater than requested load loss
18 | INSUFFICIENT AIR FLOW | Channels | Closed shutters
19 | INSUFFICIENT AIR FLOW | Channels | Obstructions in the channels
20 | INSUFFICIENT AIR FLOW | Filters | Too dirty
21 | INSUFFICIENT AIR FLOW | Coils | Too dirty
22 | EXCESSIVE AIR FLOW | Channels | Less than requested load loss
23 | EXCESSIVE AIR FLOW | Channels | Oversized channels
24 | EXCESSIVE AIR FLOW | Channels | Terminals not installed
25 | EXCESSIVE AIR FLOW | Unit | Filters not inserted
26 | EXCESSIVE AIR FLOW | Unit | Access doors open
27 | EXCESSIVE AIR FLOW | Unit | Uncelebrated shutters
28 | INSUFFICIENT HEAT YIELD | Coil | Incorrect input/output pipe connection
29 | INSUFFICIENT HEAT YIELD | Coil | Dirty coil
30 | INSUFFICIENT HEAT YIELD | Coil | Air in the pipes
31 | INSUFFICIENT HEAT YIELD | Coil | Excessive air flow
32 | INSUFFICIENT HEAT YIELD | Electrical pump | Insufficient water flow
33 | INSUFFICIENT HEAT YIELD | Electrical pump | Insufficient pressure
34 | INSUFFICIENT HEAT YIELD | Electrical pump | Wrong rotation direction
35 | INSUFFICIENT HEAT YIELD | Fluid | Temperature different from that of the design
36 | INSUFFICIENT HEAT YIELD | Fluid | Wrong adjustment organs
37 | INSUFFICIENT HUMIDIFICATION | Blocked nozzles | Lime deposits
38 | INSUFFICIENT HUMIDIFICATION | Blocked nozzles | Clogged filter
39 | INSUFFICIENT HUMIDIFICATION | Electrical pump | Wrong rotation direction
40 | INSUFFICIENT HUMIDIFICATION | Electrical pump | Lack of water in tank
41 | INSUFFICIENT HUMIDIFICATION | Electrical pump | Dirty filter pump
42 | INSUFFICIENT HUMIDIFICATION | Coil | Insufficient pre-heating
43 | INSUFFICIENT HUMIDIFICATION | Evaporating pack | Dirty, clogged or ruined pack
44 | INSUFFICIENT HUMIDIFICATION | Evaporating pack | Clogged distributor holes
45 | INSUFFICIENT HUMIDIFICATION | Non-return valve | Broken or clogged
46 | LEAKAGE OF WATER | Coil | Leakage from the coil due to corrosion
47 | LEAKAGE OF WATER | Fan section | Drips drawn due to the high speed of the air
48 | LEAKAGE OF WATER | Fan section | The overflow pipe is clogged

## Summary
Summary by Fault
Fault | No. of Causes | Main Components
EXCESSIVE NOISE | 15 | Fan rotator, Transmission, Bearings, Motor, In the channels
INSUFFICIENT AIR FLOW | 6 | Fan, Channels, Filters, Coils
EXCESSIVE AIR FLOW | 6 | Channels, Unit
INSUFFICIENT HEAT YIELD | 9 | Coil, Electrical pump, Fluid
INSUFFICIENT HUMIDIFICATION | 9 | Blocked nozzles, Electrical pump, Coil, Evaporating pack, Non-return valve
LEAKAGE OF WATER | 3 | Coil, Fan section

## Source Note
Source: HMU Maintenance Schedule.pdf, Page 1
Data manually converted from the rendered image on page 1 of the uploaded PDF.