## Troubleshooting Checklist
Systemair K 160 XL Sileo – Troubleshooting Checklist (FAMILY KITCEHN)
Symptoms | No. | Possible Cause | Corrective Action
Fan does not start | 1 | No power supply to fan. | Check incoming power supply, isolator, fuse, circuit breaker and terminal connections. Restore correct voltage before operation.
| 2 | Loose, disconnected or incorrect wiring. | Isolate power, inspect wiring against approved wiring diagram and reconnect securely.
| 3 | Integral thermal contact has tripped due to motor overheating. | Allow motor to cool, reset as per fan/control arrangement, then identify cause of overheating before restarting.
| 4 | Speed controller, 5-step transformer or control device faulty/not set. | Check controller output voltage and control setting. Repair or replace controller if no output is available.
| 5 | Motor winding damaged or motor defective. | Check winding resistance/insulation. Contact Systemair/service provider or replace motor/fan assembly as approved.
Fan stops during operation | 1 | Motor overheated and thermal protection operated. | Check airflow, ambient temperature, duct blockage, fan rotation and electrical load. Reset only after the fault is corrected.
| 2 | Voltage fluctuation, low voltage or power interruption. | Measure supply voltage during operation and correct power supply issue.
| 3 | Controller overloaded or unsuitable for fan motor. | Verify controller capacity/type is suitable for K 160 XL Sileo. Replace with approved speed control device.
| 4 | Excessive duct resistance causing high motor load. | Inspect duct, damper, filter, grille and silencer. Remove obstruction or rebalance system.
Low or insufficient airflow | 1 | Incorrect rotation direction or wrong electrical connection. | Confirm fan rotation/airflow direction against arrow on casing and correct wiring if required.
| 2 | Blocked duct, dirty grille, closed damper or clogged filter. | Clean duct/grille/filter and open/balance dampers.
| 3 | Fan speed set too low. | Increase speed through approved speed controller or transformer setting within design limits.
| 4 | High external static pressure due to long duct route or added accessories. | Measure static pressure and compare with fan selection. Reduce resistance or review fan selection.
| 5 | Air leakage in duct or poor connection to fan spigot. | Inspect joints, clamps and flexible connections. Seal leakage and tighten clamps.
Excessive noise | 1 | Fan running at high speed or system pressure too high. | Check speed setting and system static pressure. Adjust speed or rebalance duct system.
| 2 | Fan not properly fixed or bracket/clamp loose. | Tighten mounting bracket, screws and FK clamps. Ensure fan is securely supported.
| 3 | Vibration transferred to ductwork. | Install or check flexible mounting clamps/anti-vibration arrangement. Avoid rigid stress on fan casing.
| 4 | Foreign object inside impeller or duct. | Isolate power, open access, remove debris and inspect impeller for damage.
| 5 | Bearing or motor noise. | Check motor/bearing sound. If abnormal, replace fan/motor assembly or contact service.
Excessive vibration | 1 | Impeller dirty, damaged or unbalanced. | Clean impeller carefully. If damaged or still vibrating, replace impeller/fan assembly.
| 2 | Fan installed under duct stress or misalignment. | Release duct stress, realign duct connections and ensure fan casing is not twisted.
| 3 | Loose support, mounting bracket or fasteners. | Tighten all supports, brackets, clamps and fixing screws.
| 4 | Air turbulence near fan inlet/outlet. | Check installation arrangement. Provide proper straight duct/accessory arrangement as practical.
Motor overheating | 1 | Insufficient airflow over motor due to blockage or closed damper. | Clean duct/filter/grille and ensure dampers are open. Restore required airflow.
| 2 | Fan operating outside selected duty point. | Measure airflow and static pressure. Compare with approved selection and correct system resistance.
| 3 | Incorrect voltage or unstable supply. | Measure voltage and current. Correct power supply before restarting.
| 4 | Ambient temperature too high or unsuitable installation location. | Check installation condition and ventilation around fan. Relocate or improve ventilation if required.
| 5 | Frequent starts/stops or unsuitable control method. | Review control sequence and speed controller. Use approved control arrangement only.
Controller/speed control problem | 1 | Stepless thyristor or 5-step transformer not compatible or undersized. | Verify controller type and rating against fan motor data. Replace with approved Systemair-compatible controller.
| 2 | Control setting too low causing unstable operation. | Increase setting to stable operating range and confirm fan starts/runs reliably.
| 3 | Loose control wiring or poor terminal connection. | Isolate power and tighten terminals. Check continuity of control wiring.
| 4 | Controller failure. | Check input/output voltage at controller. Replace controller if faulty.
Water ingress / outdoor installation issue | 1 | Fan installed outdoors without proper weather protection or incorrect cable entry. | Check installation orientation, cable gland and terminal box sealing. Correct water path and reseal.
| 2 | Condensation or moisture accumulation in duct. | Check duct insulation, drainage and installation slope. Correct condensation source.
| 3 | Terminal box cover not properly closed. | Isolate power, dry components if needed and refit cover/gasket correctly.
Electrical protection trips | 1 | Short circuit or insulation fault. | Megger test motor and cable. Repair cable or replace motor/fan if insulation is poor.
| 2 | Overload due to blocked impeller or high static pressure. | Inspect impeller and duct system. Remove blockage and recheck running current.
| 3 | Wrong fuse/MCB rating or incorrect protection setting. | Check protection rating against approved electrical data and adjust/replace as per electrical design.
| 4 | Motor fault. | Check current, winding resistance and thermal contact. Contact service or replace fan/motor assembly.
Poor performance after maintenance | 1 | Fan reinstalled in wrong direction. | Check airflow arrow on casing and reinstall fan in correct direction.
| 2 | Duct clamp or joint not sealed after removal. | Refit clamps and seal duct joints properly.
| 3 | Accessory installed incorrectly, such as filter, silencer, grille or damper. | Check accessory orientation and cleanliness. Correct installation and rebalance airflow.
| 4 | Speed controller setting changed. | Restore approved commissioning speed setting and record final value.