## Legend
COLOUR LEGEND — ERROR CODE SERIES
Series | Location | Description
A-Series | Indoor Unit | Indoor unit mechanical faults — PCB, motors, drain, EEV, heater
C-Series | Indoor Sensors | Indoor temperature/humidity sensors and fan driver faults
E-Series | Outdoor Unit | Outdoor unit faults — compressor, fan, PCB, EEV, 4-way valve
F & H-Series | Outdoor Unit | Discharge temp, high/low pressure protection and sensor faults
J-Series | Outdoor Sensors | Outdoor thermistors and pressure transducer faults
L-Series | Inverter Drive | Inverter overcurrent, PCB, heat sink, compressor start faults
P-Series | Power / System | Phase imbalance, fin sensor and capacity setting faults
U-Series | System / Comms | Communication failures and system-level faults
Maintenance | Indoor / Outdoor | Filter reminder, defrost mode — normal operational indicators

## How To Read Error Code
HOW TO READ ERROR CODE ON DAIKIN SPLIT AC REMOTE CONTROLLER
STEP | INSTRUCTION
1 | On the Daikin remote controller, locate the CANCEL button (some models: INSPECTION/TEST button).
2 | Press and HOLD the CANCEL button for 5–6 seconds while pointing at the indoor unit.
3 | The display changes to '00' — this confirms you have entered fault-code retrieval mode.
4 | Keep pressing the CANCEL button repeatedly. Each press steps through codes with a short BEEP.
5 | When you reach the ACTUAL fault code, the unit gives a long continuous BEEP. That code on the display is your error.
6 | Note the code (e.g. U4, A5, E3) and refer to this workbook for definition and action.
7 | To EXIT the fault-code mode, hold CANCEL again for 5–6 seconds, or wait 1 minute without pressing any button.
NOTE | On some newer Daikin models the error code appears directly on the remote display screen. Simply read the code shown.
NOTE | Codes starting with A or C = Indoor Unit fault. E, F, H, J, L, P = Outdoor Unit fault. U = System / Communication fault.
NOTE | A flashing green light on the indoor unit typically signals a fault is active. Check code to identify.
NOTE | Filter LED flashing (not a fault code) = clean air filters and reset filter timer on remote.

## Full Error Code Reference
DAIKIN SPLIT AC — ERROR CODES (DISPLAYED ON REMOTE CONTROLLER)
Wall-Mounted Split & Multi-Split Inverter Systems ¦ Daikin / Airfel ¦ Source: Daikin SM-TS3 Official Malfunction Code Chart
Code | Series | Unit / Location | Error Definition | Likely Cause | Recommended Action | Split AC
A0 | A-Series | Indoor Unit | External protection device activated | External device wired to T1-T2 terminals has tripped (e.g. smoke/heat detector) | Check external protection device and T1-T2 wiring; reset once root cause resolved | ✔
A1 | A-Series | Indoor Unit | Indoor PCB defective | Main PCB failure or electrical noise causing PCB malfunction | Power cycle unit; if fault persists replace indoor PCB | ✔
A3 | A-Series | Indoor Unit | Drain level control system abnormal | Float switch open; blocked drain pipe; failed condensate pump | Clear drain line; check float switch; inspect condensate pump | ✔
A5 | A-Series | Indoor Unit | Freeze-up / high pressure protection (cooling/heating) | Clogged air filter; short circuit airflow; low refrigerant charge; EEV fault; bad coil thermistor | Clean filter; check blower; verify refrigerant charge; check indoor coil thermistor | ✔
A6 | A-Series | Indoor Unit | Fan motor malfunction | Locked rotor; overload; broken wiring or bad connector on fan motor | Check motor windings, capacitor, fan PCB and wiring; replace motor if needed | ✔
A7 | A-Series | Indoor Unit | Swing flap / louvre motor malfunction | Defective swing motor; failed PCB; damaged flap cam or connecting cable | Check louvre motor; inspect connector; replace motor or PCB as needed | ✔
A8 | A-Series | Indoor Unit | AC input overcurrent / power supply fault | Defective power supply voltage; internal short circuit in unit | Check supply voltage; inspect PCB for damage; replace if required | —
A9 | A-Series | Indoor Unit | Electronic Expansion Valve (EEV) malfunction | Defective EEV motor coil; faulty indoor PCB; damaged relay cable | Check EEV coil resistance and wiring; replace EEV or indoor PCB | ✔
AA | A-Series | Indoor Unit | Auxiliary heater overheat | Heater element overtemperature; thermal protector (26WH) activated | Check heater element and thermal protector; verify airflow across heater | —
AF | A-Series | Indoor Unit | High water level – drain blocked (thermo-off condition) | Float switch open while thermostat is OFF; drain blockage | Clear drain line; inspect float switch sensitivity | ✔
AH | A-Series | Indoor Unit | Dust collector / air cleaner malfunction | Dirty collecting element; stained insulator; failed HV power supply PCB | Clean or replace filter element; check high-voltage PCB | —
AJ | A-Series | Indoor Unit | Capacity setting error | Capacity setting adaptor not installed or incorrect adaptor fitted | Verify and install correct capacity adaptor for the unit model | ✔
C1 | C-Series | Indoor Sensor | Transmission failure – indoor main PCB to sub-PCB | Failed communication between main PCB and fan motor control driver PCB | Check connector between main and sub PCB; inspect fan control driver board | ✔
C4 | C-Series | Indoor Sensor | Liquid pipe thermistor fault (heat exchanger) | Open or short circuit in liquid pipe sensor; defective indoor PCB | Measure thermistor resistance against temperature chart; replace if faulty | ✔
C5 | C-Series | Indoor Sensor | Gas pipe thermistor fault (heat exchanger) | Open or short circuit in gas/suction pipe sensor; defective indoor PCB | Measure thermistor resistance; check connector; replace sensor or PCB | ✔
C6 | C-Series | Indoor Sensor | Fan motor sensor / fan control driver fault | Defective fan PCB; incorrect capacity adaptor; field setting error | Check fan PCB and capacity adaptor installation; replace if faulty | ✔
C7 | C-Series | Indoor Sensor | Front panel driving motor fault | Defective limit switch or front panel driving motor | Check limit switch and driving motor wiring; replace faulty component | —
C9 | C-Series | Indoor Sensor | Suction air (return air) thermistor fault | Return air sensor open or short circuit; defective indoor PCB | Measure thermistor resistance; replace sensor or PCB as needed | ✔
CA | C-Series | Indoor Sensor | Discharge air thermistor fault | Discharge air sensor open or short circuit; sensor connector loose | Check sensor connector; measure resistance; replace sensor if out of range | ✔
CC | C-Series | Indoor Sensor | Humidity sensor malfunction | Failed humidity sensor in unit | Check sensor wiring; replace humidity sensor | —
CJ | C-Series | Indoor Sensor | Remote controller room temperature sensor fault | Defective remote controller thermistor | Check remote controller sensor and wiring; replace if faulty | ✔
E0 | E-Series | Outdoor Unit | Outdoor protection device activated (unified) | Outdoor unit safety device tripped | Identify which device tripped; reset after root cause is resolved | ✔
E1 | E-Series | Outdoor Unit | Outdoor PCB defective | Defective outdoor main PCB or electrical noise interference | Check PCB for burnt components; replace outdoor PCB | ✔
E3 | E-Series | Outdoor Unit | High pressure switch (HPS) activated | Dirty condenser coil; refrigerant overcharge; outdoor fan motor failure | Clean condenser coil; check outdoor fan; verify refrigerant charge | ✔
E4 | E-Series | Outdoor Unit | Low pressure switch (LPS) activated | Refrigerant leak or shortage; restriction in refrigerant circuit | Check for leaks; inspect filter driers; verify refrigerant charge | ✔
E5 | E-Series | Outdoor Unit | Inverter compressor motor lock / overheat | Compressor mechanically locked; winding overheated; high ambient temp | Check compressor windings resistance; verify supply voltage and refrigerant charge | ✔
E6 | E-Series | Outdoor Unit | Standard compressor motor overcurrent / lock | Compressor drawing excessive current; mechanical lock | Check compressor amp draw; test motor windings; verify refrigerant charge | ✔
E7 | E-Series | Outdoor Unit | Outdoor fan motor system malfunction | Defective fan motor or outdoor PCB; motor obstruction | Check for obstruction; test motor windings; replace fan motor if faulty | ✔
E8 | E-Series | Outdoor Unit | Inverter compressor overcurrent | Compressor drawing excessive current; inverter PCB fault | Check compressor amp draw; verify refrigerant charge; check inverter PCB | ✔
E9 | E-Series | Outdoor Unit | Electronic Expansion Valve (EEV) coil malfunction | Defective EEV motor or outdoor PCB; EEV stuck open or closed | Check EEV coil resistance and wiring; replace EEV if stuck; check PCB | ✔
EA | E-Series | Outdoor Unit | Four-way valve / cool-heat switching malfunction | Defective reversing valve solenoid; PCB fault; associated sensor failure | Check solenoid coil voltage; verify valve slides between cooling and heating | ✔
F3 | F-Series | Outdoor Unit | Discharge pipe temperature too high | Discharge temperature exceeded limit; low refrigerant; restriction in circuit | Check refrigerant charge; inspect EEV; check discharge pipe thermistor | ✔
F6 | F-Series | Outdoor Unit | Abnormal high pressure / refrigerant overcharge | Refrigerant overcharged; dirty outdoor coil; outdoor fan issue | Verify refrigerant charge; clean condenser coil; check fan operation | ✔
H0 | H-Series | Outdoor Unit | Compressor sensor system malfunction (unified) | All compressor-related sensors disconnected simultaneously | Check all sensor connectors on outdoor PCB; reseat or replace | ✔
H3 | H-Series | Outdoor Unit | High pressure switch (HPS) fault – open circuit | HP switch failed open; wiring fault | Measure continuity of HP switch; replace if failed open | ✔
H4 | H-Series | Outdoor Unit | Low pressure switch (LPS) fault – open circuit | LP switch failed open; wiring fault | Measure continuity of LP switch; replace if failed open | ✔
H6 | H-Series | Outdoor Unit | Compressor position detection sensor malfunction | Inverter position detection error; inverter PCB or compressor feedback fault | Check inverter board and compressor position feedback wiring | ✔
H7 | H-Series | Outdoor Unit | Outdoor fan motor signal malfunction | Defective fan motor position sensor or outdoor PCB | Check fan motor and signal wiring to PCB; replace faulty component | ✔
H8 | H-Series | Outdoor Unit | Compressor input current (CT) sensor malfunction | Defective power transistor; PCB fault; reactor failure | Check inverter PCB current sensing circuit; replace if defective | ✔
H9 | H-Series | Outdoor Sensor | Outdoor air thermistor malfunction | Ambient sensor open or short circuit; defective PCB | Measure thermistor resistance vs temperature chart; replace if out of range | ✔
J1 | J-Series | Outdoor Sensor | Pressure sensor malfunction | Pressure transducer failed; defective PCB | Check pressure sensor wiring; replace sensor if out of range | ✔
J3 | J-Series | Outdoor Sensor | Discharge pipe thermistor fault | Discharge pipe sensor open or short circuit; loose connector | Measure sensor resistance; check connector; replace thermistor | ✔
J5 | J-Series | Outdoor Sensor | Suction pipe thermistor fault | Suction pipe sensor open or short circuit | Measure resistance; check connector; replace thermistor if faulty | ✔
J6 | J-Series | Outdoor Sensor | Outdoor heat exchanger thermistor fault | Coil sensor open or short circuit | Measure resistance against temperature chart; replace if out of range | ✔
J7 | J-Series | Outdoor Sensor | Liquid pipe thermistor fault (outdoor) | Liquid pipe sensor open or short circuit | Check sensor connector; replace thermistor | ✔
J9 | J-Series | Outdoor Sensor | Sub-cool heat exchanger thermistor fault | Sub-cooler sensor open or short circuit | Measure resistance; replace thermistor; check PCB connector | ✔
JA | J-Series | Outdoor Sensor | High pressure transducer malfunction | HP transducer open or short circuit; wiring fault | Check transducer wiring and output voltage; replace if faulty | ✔
JC | J-Series | Outdoor Sensor | Low pressure transducer malfunction | LP transducer open or short circuit; wiring fault | Check transducer wiring and output voltage; replace if faulty | ✔
L1 | L-Series | Inverter | Inverter PCB defective | Blown fuse; defective inverter PCB; failed fan motor | Check inverter fuses; replace inverter PCB if confirmed defective | ✔
L4 | L-Series | Inverter | Inverter heat sink temperature rise (fin temp >93°C) | Blocked airflow at heat sink; failed fin sensor; short circuit | Clear airflow path; clean heat sink fins; check fin temperature sensor | ✔
L5 | L-Series | Inverter | Inverter instantaneous DC overcurrent | Defective inverter PCB; compressor winding fault; compressor lock | Check compressor insulation resistance; inspect inverter PCB power section | ✔
L8 | L-Series | Inverter | Inverter compressor overcurrent | Inverter PCB defect; compressor lock or winding fault | Check compressor amp draw; inspect inverter PCB | ✔
L9 | L-Series | Inverter | Inverter compressor start-up failure | Defective inverter PCB; compressor lock; low refrigerant charge | Check refrigerant charge; test compressor; replace inverter PCB if confirmed | ✔
LC | L-Series | Inverter | Transmission failure – main PCB to inverter PCB | Noise; defective inverter PCB; main PCB; fan PCB; noise filter failure | Check all PCB connectors; replace inverter or main PCB if defective | ✔
P1 | P-Series | Outdoor Unit | Power supply voltage imbalance / open phase | Open phase; voltage imbalance between phases; defective main capacitor | Check 3-phase supply voltages; verify main capacitor; inspect inverter PCB | ✔
P4 | P-Series | Outdoor Sensor | Inverter radiation fin temperature sensor fault | Fin temperature sensor open or short circuit | Measure fin sensor resistance; replace sensor | ✔
PJ | P-Series | Outdoor Unit | Capacity setting not set or error | Capacity setting adaptor not fitted; incorrect setting on outdoor PCB | Verify and install correct capacity setting adaptor | ✔
U0 | U-Series | System | Refrigerant shortage detected | System undercharged; EEV fault; faulty pressure or temperature sensor | Check for refrigerant leaks; verify charge; check EEV and sensors | ✔
U1 | U-Series | System | Reverse phase / open phase | Reversed phase sequence; missing phase in 3-phase power supply | Check phase sequence with meter; verify all 3 phases present and correct | ✔
U2 | U-Series | System | Power supply fault / instantaneous power failure | Power supply voltage fault; capacitor wiring error; power failure | Check power supply voltage stability; check capacitor wiring; verify earthing | ✔
U3 | U-Series | System | Check operation not executed | Commissioning check operation not performed after installation or PCB replacement | Run check operation from remote controller in test / inspection mode | ✔
U4 | U-Series | System | Communication failure – indoor to outdoor unit | Wiring fault on F1/F2 transmission wiring; defective PCB; pump wired across comms | Check F1/F2 wiring polarity and continuity; remove any external device across terminals | ✔
U5 | U-Series | System | Communication failure – remote controller to indoor PCB | Wiring fault between remote controller and indoor PCB; defective controller or PCB | Check remote controller wiring and connections; swap controller to test | ✔
U8 | U-Series | System | Communication failure – between remote controllers | Main/sub switch not set correctly; wiring error; defective remote controller | Verify main/sub controller setting; check wiring | ✔
U9 | U-Series | System | System communication failed | Fault in another indoor unit (e.g. A9); no power to unit; system-wide comms issue | Check all indoor units for individual faults; verify power to all units | ✔
UA | U-Series | System | Improper combination / field setting error | Excess indoor units connected; incorrect PCB setting; capacity mismatch | Verify total indoor capacity ≤ outdoor capacity; check all field settings | ✔
UF | U-Series | System | Wiring / piping mismatch detected | Indoor-to-outdoor wiring error; PCB defect | Verify F1/F2 wiring is correct indoor to outdoor; run check operation | ✔
UH | U-Series | System | System malfunction | Unaddressed indoor unit; indoor/outdoor mismatch; freeze protection active | Check all unit addresses; verify indoor-outdoor compatibility | ✔
— (Filter LED) | Maintenance | Indoor Unit | Filter cleaning reminder | Filter running hours reached cleaning interval (default ~250 hrs) | Clean air filters; reset filter timer via remote controller | ✔
— (Defrost) | Maintenance | Outdoor Unit | Defrost mode active (not an error) | Outdoor coil temperature dropped to defrost threshold – normal winter operation | Wait for defrost cycle to complete (approx 5–10 min); unit resumes automatically | ✔

## Quick Lookup
DAIKIN SPLIT AC — QUICK ERROR CODE LOOKUP
Wall-Mounted Split & Multi-Split ¦ Daikin / Airfel
Code | Series | Short Definition | Top Cause | Split AC?
A0 | A-Series | External protection device activated | External device wired to T1-T2 terminals has tripped (e.g. smoke/heat detector) | ✔
A1 | A-Series | Indoor PCB defective | Main PCB failure or electrical noise causing PCB malfunction | ✔
A3 | A-Series | Drain level control system abnormal | Float switch open | ✔
A5 | A-Series | Freeze-up / high pressure protection (cooling/heating) | Clogged air filter | ✔
A6 | A-Series | Fan motor malfunction | Locked rotor | ✔
A7 | A-Series | Swing flap / louvre motor malfunction | Defective swing motor | ✔
A8 | A-Series | AC input overcurrent / power supply fault | Defective power supply voltage | —
A9 | A-Series | Electronic Expansion Valve (EEV) malfunction | Defective EEV motor coil | ✔
AA | A-Series | Auxiliary heater overheat | Heater element overtemperature | —
AF | A-Series | High water level – drain blocked (thermo-off condition) | Float switch open while thermostat is OFF | ✔
AH | A-Series | Dust collector / air cleaner malfunction | Dirty collecting element | —
AJ | A-Series | Capacity setting error | Capacity setting adaptor not installed or incorrect adaptor fitted | ✔
C1 | C-Series | Transmission failure – indoor main PCB to sub-PCB | Failed communication between main PCB and fan motor control driver PCB | ✔
C4 | C-Series | Liquid pipe thermistor fault (heat exchanger) | Open or short circuit in liquid pipe sensor | ✔
C5 | C-Series | Gas pipe thermistor fault (heat exchanger) | Open or short circuit in gas/suction pipe sensor | ✔
C6 | C-Series | Fan motor sensor / fan control driver fault | Defective fan PCB | ✔
C7 | C-Series | Front panel driving motor fault | Defective limit switch or front panel driving motor | —
C9 | C-Series | Suction air (return air) thermistor fault | Return air sensor open or short circuit | ✔
CA | C-Series | Discharge air thermistor fault | Discharge air sensor open or short circuit | ✔
CC | C-Series | Humidity sensor malfunction | Failed humidity sensor in unit | —
CJ | C-Series | Remote controller room temperature sensor fault | Defective remote controller thermistor | ✔
E0 | E-Series | Outdoor protection device activated (unified) | Outdoor unit safety device tripped | ✔
E1 | E-Series | Outdoor PCB defective | Defective outdoor main PCB or electrical noise interference | ✔
E3 | E-Series | High pressure switch (HPS) activated | Dirty condenser coil | ✔
E4 | E-Series | Low pressure switch (LPS) activated | Refrigerant leak or shortage | ✔
E5 | E-Series | Inverter compressor motor lock / overheat | Compressor mechanically locked | ✔
E6 | E-Series | Standard compressor motor overcurrent / lock | Compressor drawing excessive current | ✔
E7 | E-Series | Outdoor fan motor system malfunction | Defective fan motor or outdoor PCB | ✔
E8 | E-Series | Inverter compressor overcurrent | Compressor drawing excessive current | ✔
E9 | E-Series | Electronic Expansion Valve (EEV) coil malfunction | Defective EEV motor or outdoor PCB | ✔
EA | E-Series | Four-way valve / cool-heat switching malfunction | Defective reversing valve solenoid | ✔
F3 | F-Series | Discharge pipe temperature too high | Discharge temperature exceeded limit | ✔
F6 | F-Series | Abnormal high pressure / refrigerant overcharge | Refrigerant overcharged | ✔
H0 | H-Series | Compressor sensor system malfunction (unified) | All compressor-related sensors disconnected simultaneously | ✔
H3 | H-Series | High pressure switch (HPS) fault – open circuit | HP switch failed open | ✔
H4 | H-Series | Low pressure switch (LPS) fault – open circuit | LP switch failed open | ✔
H6 | H-Series | Compressor position detection sensor malfunction | Inverter position detection error | ✔
H7 | H-Series | Outdoor fan motor signal malfunction | Defective fan motor position sensor or outdoor PCB | ✔
H8 | H-Series | Compressor input current (CT) sensor malfunction | Defective power transistor | ✔
H9 | H-Series | Outdoor air thermistor malfunction | Ambient sensor open or short circuit | ✔
J1 | J-Series | Pressure sensor malfunction | Pressure transducer failed | ✔
J3 | J-Series | Discharge pipe thermistor fault | Discharge pipe sensor open or short circuit | ✔
J5 | J-Series | Suction pipe thermistor fault | Suction pipe sensor open or short circuit | ✔
J6 | J-Series | Outdoor heat exchanger thermistor fault | Coil sensor open or short circuit | ✔
J7 | J-Series | Liquid pipe thermistor fault (outdoor) | Liquid pipe sensor open or short circuit | ✔
J9 | J-Series | Sub-cool heat exchanger thermistor fault | Sub-cooler sensor open or short circuit | ✔
JA | J-Series | High pressure transducer malfunction | HP transducer open or short circuit | ✔
JC | J-Series | Low pressure transducer malfunction | LP transducer open or short circuit | ✔
L1 | L-Series | Inverter PCB defective | Blown fuse | ✔
L4 | L-Series | Inverter heat sink temperature rise (fin temp >93°C) | Blocked airflow at heat sink | ✔
L5 | L-Series | Inverter instantaneous DC overcurrent | Defective inverter PCB | ✔
L8 | L-Series | Inverter compressor overcurrent | Inverter PCB defect | ✔
L9 | L-Series | Inverter compressor start-up failure | Defective inverter PCB | ✔
LC | L-Series | Transmission failure – main PCB to inverter PCB | Noise | ✔
P1 | P-Series | Power supply voltage imbalance / open phase | Open phase | ✔
P4 | P-Series | Inverter radiation fin temperature sensor fault | Fin temperature sensor open or short circuit | ✔
PJ | P-Series | Capacity setting not set or error | Capacity setting adaptor not fitted | ✔
U0 | U-Series | Refrigerant shortage detected | System undercharged | ✔
U1 | U-Series | Reverse phase / open phase | Reversed phase sequence | ✔
U2 | U-Series | Power supply fault / instantaneous power failure | Power supply voltage fault | ✔
U3 | U-Series | Check operation not executed | Commissioning check operation not performed after installation or PCB replacement | ✔
U4 | U-Series | Communication failure – indoor to outdoor unit | Wiring fault on F1/F2 transmission wiring | ✔
U5 | U-Series | Communication failure – remote controller to indoor PCB | Wiring fault between remote controller and indoor PCB | ✔
U8 | U-Series | Communication failure – between remote controllers | Main/sub switch not set correctly | ✔
U9 | U-Series | System communication failed | Fault in another indoor unit (e.g. A9) | ✔
UA | U-Series | Improper combination / field setting error | Excess indoor units connected | ✔
UF | U-Series | Wiring / piping mismatch detected | Indoor-to-outdoor wiring error | ✔
UH | U-Series | System malfunction | Unaddressed indoor unit | ✔
— (Defrost) | Maintenance | Defrost mode active (not an error) | Outdoor coil temperature dropped to defrost threshold – normal winter operation | ✔
— (Filter LED) | Maintenance | Filter cleaning reminder | Filter running hours reached cleaning interval (default ~250 hrs) | ✔