## KN86N3 Error Codes
ERROR CODES THERMOSTAT KN-86N3
LOCATION | MAIN KITCEHN STORAGE AREA SPLIT AC
1. Debugging
Displayed code | Definition
A0 | The system is not debugged
A2 | Oil return of system
A4 | Rated capacity test
A6 | IPLV2 test
A8 | Module refrigerant recovery
AA | System setting
AC | Cooling mode
AE | Manual perfusion
AJ | Main board hardware self-test
AU | Self-cleaning mode
n0 | Query fault history of unit
n2 | Query setting state of unit
n4 | Cooling and heating function setting
n6 | Energy saving operation setting of system
n8 | Forced defrosting
nA | Cooling and heating
nC | Cooling only
nF | FanOnly
2. Protection/fault of indoor unit
Code | Definition
d1 | Protection of indoor fan
d3 | Water full protection
d5 | Mode conflict
d7 | Capacity dial error
d9 | Wired control IP address conflict
b1 | Ambient temperature sensor fault
b3 | Middle temperature sensor fault
b5 | Humidity sensor fault
b7 | Indoor EEPROM fault
b9 | Abnormal MAC address of indoor unit
3. Protection/fault of outdoor unit
Code | Definition
L1 | Tp1 exhaust temperature sensor failed or fell off
L3 | Tp3 constant-frequency compressor exhaust sensing bulb 1 / Variable-frequency compressor exhaust sensing bulb 2 sensor fault
L5 | Tp5 oil return sensing bulb 1 sensor fault
L7 | Tp7 condenser gas collector temperature 2 sensor fault
L9 | T3A defrosting sensor fault
LH | Tq1 gas inlet pipe sensor fault
LL | T-g subcooler air outlet sensor fault
LF | SHP high-pressure sensor fault
LP | Abnormal MAC address of outdoor unit
Ld | Tsj subcooler air inlet sensor fault
4. System protection
Code | Definition
H0 | Total fault of outdoor unit (including protection)
H2 | Protection for low pressure
H4 | Protection for too high pressure ratio
H6 | Protection for system in lack of refrigerant
H8 | Overcurrent protection for constant-frequency compressor 1
HA | Overcurrent protection for constant-frequency compressor 3
HC | Overcurrent protection for constant-frequency compressor 5
HE | Protection for power phase sequence
5. Others
Code | Definition
U1 | Module emergency dial error
U3 | Emergency state of variable-frequency compressor
U5 | Emergency state of variable-frequency fan
U7 | Too high rated capacity ratio
U9 | Abnormal valve/pipeline of unit
UH | Protection for four-way valve with commutation fault
UL | Dialing error fault of outdoor unit model
6. Driving faults of compressor
Code | Definition
J0 | Total fault of operation of variable-frequency compressor
J2 | Driving failure of compressor
J4 | Input voltage phase loss
J6 | Radiator shutdown due to overheat
J8 | DC bus overvoltage
JA | Protection for abnormal AC input voltage
JC | Input voltage sampling fault
JE | Temperature sensor fault
JJ | Compressor phase loss
7. Driving faults of fan
Code | Definition
F0 | Fan 1 operation fault
F2 | Variable-frequency fan overcurrent protection (displayed by outdoor unit)
F4 | Fan-driven temperature sensor fault (displayed by outdoor unit)
F6 | Fan-driven memory chip fault (displayed by outdoor unit)
F8 | Fan-driven current detection circuit fault (displayed by outdoor unit)
FA | Variable-frequency fan phase fault (displayed by outdoor unit)
FC | Variable-frequency fan start fault (displayed by outdoor unit)
Communication fault
Code | Definition
C0 | Total fault of CAN communication fault
C2 | Abnormal number of external unit modules (missing/increasing)
C4 | Communication fault of main control and the variable-frequency fan drive (displayed by the external unit)
C6 | Indoor unit missing fault
C1 | Fan-driven temperature sensor fault
C3 | Communication fault between main control and variable-frequency compressor drive (displayed by outdoor unit)
C5 | Communication fault between the internal unit and the wired control (displayed on the internal unit)