## Indoor Unit Error Codes
VRF SYSTEM — INDOOR UNIT ERROR CODES
Reference: Manufacturer Malfunction Code Table ¦ CEO Villa Project
Main Code | Description / Fault | Location
A0 | External protection device was activated | Indoor
A1 | EEPROM failure | Indoor
A3 | Drain system malfunction | Indoor
A5 | Fan motor malfunction | Indoor
A7 | Swing flap motor malfunction | Indoor
A9 | Expansion valve malfunction | Indoor
AF | Drain malfunction | Indoor
AH | Filter dust chamber malfunction | Indoor
AJ | Capacity setting malfunction | Indoor
C1 | Transmission malfunction — Main PCB ↔ Sub PCB | Indoor
C4 | Heat exchanger thermistor malfunction (liquid side) | Indoor
C5 | Heat exchanger thermistor malfunction (gas side) | Indoor
C9 | Suction air thermistor malfunction | Indoor
C8 | Discharge air thermistor malfunction | Indoor
CE | Movement detector / floor temperature sensor fault | Indoor
CJ | User interface thermistor malfunction | Indoor
NOTES & OPERATING GUIDELINES
Safety Devices | If a fuse, breaker, or earth leakage breaker frequently actuates, or the ON/OFF switch does not work properly — turn off the MAIN POWER SWITCH immediately.
Water Leakage | If water leaks from the unit, stop the operation immediately and investigate the drain line and condensate tray.
Control Switch | If the operation switch does not work, turn off the power and contact the installer.
Malfunction Code | When the user interface display shows the unit number with a flashing operation lamp and a malfunction code — note the code and notify the installer.
No Operation | Check for power failure; wait for supply restoration. The system auto-restarts after power recovery. Also verify no fuse has blown or breaker tripped.
Fan Only / Stops | If the unit runs in fan-only mode but stops when switching to heating/cooling — check for blocked air inlet/outlet on indoor or outdoor unit. Also check if air filter cleaning indicator is active.
Insufficient C/H | Check for blocked airflow, clogged filter, incorrect temperature/fan speed settings, open doors/windows, excessive occupants or heat sources, direct sunlight, and improper airflow angle.
Error Code Reset | Depending on the malfunction level, you may reset the code by pressing the ON/OFF button. If reset is not possible, contact the installer with: Malfunction Code + Unit Type + Serial Number (from nameplate).

## Outdoor Unit Error Codes
VRF SYSTEM — OUTDOOR UNIT ERROR CODES
Reference: Manufacturer Malfunction Code Table ¦ CEO Villa Project
Main Code | Description / Fault | Location
E1 | PCB malfunction | Outdoor
E2 | Current leakage detector activated | Outdoor
E3 | High pressure switch activated | Outdoor
E4 | Low pressure malfunction | Outdoor
E5 | Compressor lock detection | Outdoor
E7 | Fan motor malfunction | Outdoor
E9 | Electronic expansion valve malfunction | Outdoor
F3 | Discharge temperature malfunction | Outdoor
F4 | Abnormal suction temperature | Outdoor
F6 | Refrigerant overcharge detection | Outdoor
H3 | High pressure switch malfunction | Outdoor
H4 | Low pressure switch malfunction | Outdoor
H7 | Fan motor trouble | Outdoor
H9 | Ambient temperature sensor malfunction (R1T) | Outdoor
J1 | Pressure sensor malfunction | Outdoor
J2 | Current sensor malfunction | Outdoor
J3 | Discharge temperature sensor malfunction (R21T) | Outdoor
J4 | Heat exchanger gas temperature sensor malfunction | Outdoor
J5 | Suction temperature sensor malfunction (R3T) | Outdoor
J6 | De-icing temperature sensor malfunction (R7T) | Outdoor
J7 | Liquid temperature sensor — after subcool HE (R5T) | Outdoor
J8 | Liquid temperature sensor — coil (R4T) | Outdoor
J9 | Gas temperature sensor — after subcool HE (R6T) | Outdoor
JA | High pressure sensor malfunction (S1NPH) | Outdoor
JC | Low pressure sensor malfunction (S1NPL) | Outdoor
L1 | INV PCB abnormal | Outdoor
L4 | Fin temperature abnormal | Outdoor
L5 | Inverter PCB faulty | Outdoor
L8 | Compressor over current detected | Outdoor
L9 | Compressor lock (startup) | Outdoor
LC | INV transmission trouble — outdoor ↔ inverter | Outdoor
P1 | INV unbalanced power supply voltage | Outdoor
P4 | Fin thermistor malfunction | Outdoor
PJ | Capacity setting malfunction | Outdoor

## System & Communication Errors
VRF SYSTEM — SYSTEM & COMMUNICATION ERROR CODES
Reference: Manufacturer Malfunction Code Table ¦ CEO Villa Project
Main Code | Description / Fault | Category
U0 | Abnormal low pressure drop — faulty expansion valve | System
U1 | Reversed power supply phase malfunction | Power
U2 | INV voltage power shortage | Power
U3 | System test run not yet executed | System
U4 | Faulty wiring — indoor / outdoor | Wiring
U5 | Abnormal user interface ↔ indoor communication | Communication
U7 | Faulty wiring — outdoor / outdoor | Wiring
U8 | Abnormal main-sub user interface communication | Communication
U9 | System mismatch — wrong type of indoor units combined | System
UA | Connection malfunction over indoor units or type mismatch | System
UC | Centralised address duplication | Communication
UE | Malfunction in communication — centralised control ↔ indoor | Communication
UF | Auto address malfunction (inconsistency) | Communication
UH | Auto address malfunction (inconsistency) | Communication
TROUBLESHOOTING PROCEDURE — TEST RUN & ERROR CODE READING
Test Run Steps | Control before start-up (pressure equalisation) → Cooling start-up control → Cooling stable condition → Communication check → Stop valve check → Pipe length check → Refrigerant amount check → Pump-down operation → Unit stop.
Normal Completion | No indication on the 7-segment display (idle state). Normal operation will be available 5 minutes after test run completes successfully.
Abnormal Completion | Malfunction code is indicated on the 7-segment display. Refer to Section 7.5 — Correcting after abnormal completion of the test run.
Code Display Format | The outdoor unit 7-segment display shows MAIN CODE and SUB CODE alternately with a 1-second interval. Sub code provides more detailed fault information.
Corrective Action | After identifying and correcting the fault, press BS3 to RESET the malfunction code, then retry operation.
Stop Valve Errors | Many error codes (E3, E4, F3, F6, FB) are caused by closed stop valves or refrigerant shortage. Always check stop valve positions first before deeper investigation.
Wiring Checks | For U4, U7, U5, U8 — always check Q1/Q2 wiring connections between indoor and outdoor units. Verify all field wiring against the installation diagram.
Type Mismatch | U9, UA errors indicate incompatible indoor unit types (R410A, R407C, RA, Hydrobox, etc.) are combined. Confirm the permitted indoor unit mix with the manufacturer before installation.

## Detailed Cause & Solution
VRF SYSTEM — DETAILED ERROR CODES WITH CAUSE & SOLUTION
Reference: Outdoor Unit Troubleshooting Manual — Section 8.2 ¦ CEO Villa Project
Main Code | Sub Code (Master) | Cause | Solution | Component Ref.
E2 | -06 | Earth leakage detector activated | Restart the unit. If problem recurs, contact the dealer. | —
E3 | -01 | High pressure switch activated (S1PH, S2PH) — A1P (X3A; X4A) | Check stop valve status or abnormalities in field piping / airflow over coil. | S1PH, S2PH
E3 | -02 | Refrigerant overcharge / Stop valve closed | Check refrigerant amount & recharge. Open stop valves. | —
E3 | -13 | Stop valve closed (liquid side) | Open liquid stop valve. | —
E4 | -01 | Low pressure malfunction — stop valve closed / refrigerant shortage | Open stop valves. Check refrigerant amount. Check UI display & wiring. | —
E9 | -01 | Electronic expansion valve malfunction — subcool (Y2E) — A1P (X21A) | Check connection on PCB or actuator. | Y2E / X21A
E9 | -04 | Electronic expansion valve malfunction — main (Y1E) — A1P (X23A) | Check connection on PCB or actuator. | Y1E / X23A
F3 | -01 | Discharge temperature too high (R21T/R22T) — stop valve / refrig. shortage | Open stop valves. Check refrigerant amount and recharge. | R21T, R22T
F3 | -20 | Compressor casing temperature too high (R8T) | Open stop valves. Check refrigerant amount and recharge. | R8T
F6 | — | Refrigerant overcharge / Stop valve closed | Check refrigerant amount. Open stop valves. | —
H9 | -01 | Ambient temperature sensor malfunction (R1T) — A1P (X18A) | Check connection on PCB or actuator. | R1T / X18A
J3 | -16 | Discharge temperature sensor malfunction — R21T open circuit — A1P (X29A) | Check connection on PCB or actuator. | R21T / X29A
J3 | -17 | Discharge temperature sensor malfunction — R21T short circuit | Check connection on PCB or actuator. | R21T / X29A
J5 | -01 | Suction temperature sensor malfunction (R3T) — A1P (X30A) | Check connection on PCB or actuator. | R3T / X30A
J6 | -01 | De-icing temperature sensor malfunction (R7T) — A1P (X30A) | Check connection on PCB or actuator. | R7T / X30A
J7 | -06 | Liquid temp sensor — after subcool HE (R5T) — A1P (X30A) | Check connection on PCB or actuator. | R5T / X30A
J8 | -01 | Liquid temperature sensor — coil (R4T) — A1P (X30A) | Check connection on PCB or actuator. | R4T / X30A
J9 | -01 | Gas temp sensor — after subcool HE (R6T) — A1P (X30A) | Check connection on PCB or actuator. | R6T / X30A
JA | -06 | High pressure sensor malfunction — S1NPH open circuit — A1P (X32A) | Check connection on PCB or actuator. | S1NPH / X32A
JC | -06 | Low pressure sensor malfunction — S1NPL open circuit — A1P (X31A) | Check connection on PCB or actuator. | S1NPL / X31A
LC | -14 | INV1 transmission trouble — outdoor ↔ inverter — A1P (X20A/X28A/X40A) | Check connection. | X20A/X28A/X40A
P1 | -01 | INV1 unbalanced power supply voltage | Check if power supply is within specification range. | INV1
U1 | -01 | Reversed power supply phase malfunction | Correct phase order. | —
U2 | -01 | INV1 voltage power shortage | Check if power supply is within specification range. | INV1
U2 | -02 | INV1 power phase loss | Check if power supply is within specification range. | INV1
U3 | -03 | System test run not yet executed | Execute system test run before operation. | —
U4 | -01 | Faulty wiring — indoor to outdoor (Q1/Q2) | Check Q1/Q2 wiring connections. | Q1/Q2
U9 | -01 | System mismatch — wrong indoor unit types combined | Check for indoor unit malfunction; confirm permitted unit mix. | —
UH | -01 | Auto address malfunction (inconsistency) | Verify transmission wired unit count matches powered unit count (monitor mode). | —
UF | -05 | Stop valve closed or wrong (during system test run) | Open stop valves. | —