## Series Legend
ERROR CODE SERIES GUIDE
Series | Location / Unit | Description | Colour
A-Series | Indoor Unit | Indoor unit mechanical and electrical faults | ◼ Sample colour
C-Series | Indoor Sensors | Indoor temperature and humidity sensor faults | ◼ Sample colour
E-Series | Outdoor Unit | Outdoor unit faults — compressor, fan, PCB, valves | ◼ Sample colour
F-Series | Outdoor Unit | High discharge temp and pressure protection faults | ◼ Sample colour
H-Series | Outdoor Unit | Pressure switch, sensor and inverter protection faults | ◼ Sample colour
J-Series | Outdoor Sensors | Outdoor thermistors and pressure transducer faults | ◼ Sample colour
L-Series | Inverter / Outdoor | Inverter drive faults — overcurrent, PCB, compressor | ◼ Sample colour
P-Series | Outdoor / System | Phase imbalance, heat sink and capacity setting faults | ◼ Sample colour
U-Series | System Wide | Communication and system-level faults | ◼ Sample colour
M-Series | Central Control | Central controller and BMS communication faults | ◼ Sample colour
6x-Series | HRV / Legacy | Legacy / HRV unit sensor and damper faults | ◼ Sample colour

## Full Error Code Reference
DAIKIN VRV SYSTEM — COMPLETE ERROR CODE REFERENCE
System: FSXQ-A Indoor Unit ¦ RXYTQ Outdoor Unit ¦ Madoka BRC1H81W Controller
Code | Series | Unit / Location | Definition | Likely Cause / Check | Action / Solution | Applies To VRV
A0 | A-Series | Indoor Unit | External protection device active | External protection wired to T1-T2 terminals is active | Check external protection device and wiring on T1-T2; reset if tripped | ✔
A1 | A-Series | Indoor Unit | Indoor PCB failure | Defective PCB or electrical noise interference | Reset power supply; if fault persists replace indoor unit PCB | ✔
A3 | A-Series | Indoor Unit | High water level / drain fault | Float switch open circuit; blocked drain pipe or failed drain pump | Clear drain line; check float switch and drain pump operation | ✔
A5 | A-Series | Indoor Unit | Freeze-up / high pressure protection | Poor airflow, short circuit, EEV fault, low refrigerant, bad coil thermistor | Clean air filters; check blower; verify refrigerant charge; check indoor coil thermistor | ✔
A6 | A-Series | Indoor Unit | Indoor fan motor failure | Locked rotor, overcurrent, overload, broken wiring or bad connector | Check motor windings, capacitor, fan PCB and wiring harness; replace motor if faulty | ✔
A7 | A-Series | Indoor Unit | Louvre / swing flap motor failure | Defective louvre motor, indoor PCB, or connecting cable; flap cam damaged | Check louvre motor operation; check connectors; replace motor or PCB as needed | ✔
A8 | A-Series | Indoor Unit | Power supply / AC input overcurrent | Defective power supply voltage; internal short circuit | Check power supply voltage and wiring; replace PCB if internal fault confirmed | —
A9 | A-Series | Indoor Unit | Electronic Expansion Valve (EEV) failure | Defective EEV motor coil, indoor PCB, or relay cable | Check EEV coil resistance and wiring; replace EEV or indoor PCB as needed | ✔
AA | A-Series | Indoor Unit | Heater overheat | Auxiliary heater overtemperature; 26WH thermal protector activated | Check heater element and thermal protector; verify airflow across heater | —
AF | A-Series | Indoor Unit | High water level (thermo-off condition) | Float switch open circuit while thermostat is OFF; drain blockage | Inspect and clear drain; check float switch sensitivity | ✔
AH | A-Series | Indoor Unit | Air filter / dust collector malfunction | Defective dust collecting element; stained insulator; failed HV power supply PCB | Clean or replace filter element; check high-voltage power supply PCB | ✔
AJ | A-Series | Indoor Unit | Capacity setting error | Capacity setting adaptor not installed or incorrect adaptor fitted | Verify correct capacity adaptor is installed matching unit specifications | ✔
C1 | C-Series | Indoor Unit | Communication failure — main to sub PCB | Failed communication between main PCB and fan motor control driver sub-PCB | Check connector between main and sub PCB; check fan control driver board | ✔
C4 | C-Series | Indoor Sensor | Indoor coil thermistor fault (liquid pipe) | Open or short circuit in liquid pipe thermistor; defective indoor PCB | Measure thermistor resistance (compare to chart); replace thermistor or PCB if faulty | ✔
C5 | C-Series | Indoor Sensor | Suction / gas pipe thermistor fault | Open or short circuit in suction pipe thermistor; defective indoor PCB | Measure thermistor resistance; check connector; replace as needed | ✔
C6 | C-Series | Indoor Unit | Fan motor sensor / driver failure | Defective fan PCB or capacity setting adaptor; field setting error | Check fan PCB and capacity adaptor installation; replace if faulty | ✔
C7 | C-Series | Indoor Sensor | Front panel / louver position sensor fault | Defective limit switch or front panel driving motor | Check limit switch and driving motor wiring; replace faulty component | —
C9 | C-Series | Indoor Sensor | Return air temperature thermistor fault | Return air sensor open or short circuit; defective indoor PCB | Measure thermistor resistance; replace sensor or PCB as needed | ✔
CA | C-Series | Indoor Sensor | Discharge air thermistor fault | Discharge air sensor open or short circuit; sensor disconnected | Check sensor connector and measure resistance; replace sensor if out of range | ✔
CC | C-Series | Indoor Sensor | Humidity sensor failure | Failed humidity sensor in unit | Check sensor wiring; replace humidity sensor | —
CJ | C-Series | Indoor Sensor | Remote temperature sensor failure | Defective remote controller sensor | Check remote sensor wiring and resistance; replace if faulty | ✔
E0 | E-Series | Outdoor Unit | Outdoor protection device tripped | Outdoor unit safety device (thermal, pressure) activated | Identify which device tripped; reset after root cause resolved | ✔
E1 | E-Series | Outdoor Unit | Outdoor PCB failure | Defective outdoor main PCB or electrical noise | Check PCB for burnt components; replace outdoor PCB if fault confirmed | ✔
E3 | E-Series | Outdoor Unit | High pressure switch tripped | Dirty condenser coil; refrigerant overcharge; outdoor fan motor failure | Clean condenser; check fan operation; verify refrigerant charge | ✔
E4 | E-Series | Outdoor Unit | Low pressure switch tripped | Refrigerant leak; restriction in refrigerant circuit; defective compressor | Check for refrigerant leaks; inspect filter driers; verify charge | ✔
E5 | E-Series | Outdoor Unit | Inverter compressor locked / overheated | Compressor mechanically locked; windings overheated; high ambient temperature | Check compressor windings resistance; verify supply voltage; check refrigerant charge | ✔
E6 | E-Series | Outdoor Unit | Fan motor locked / high current (DOL) | Fan motor stuck; debris obstruction; motor drawing excessive current | Check for obstruction around fan; test motor windings and capacitor; replace if faulty | ✔
E7 | E-Series | Outdoor Unit | Outdoor fan motor failure | Defective fan motor or outdoor PCB; wiring fault | Check fan motor electrical connections and PCB; replace faulty motor | ✔
E8 | E-Series | Outdoor Unit | Inverter compressor high current | Compressor drawing excessive current; inverter PCB or compressor defect | Check compressor amp draw; verify refrigerant charge; check inverter PCB | ✔
E9 | E-Series | Outdoor Unit | Outdoor EEV motor failure | Defective EEV motor or outdoor PCB; EEV stuck open or closed | Check EEV coil resistance and wiring; replace EEV if stuck; check PCB | ✔
EA | E-Series | Outdoor Unit | 4-way valve abnormality | Defective reversing valve solenoid, PCB, or associated sensor | Check solenoid coil voltage; verify valve slides; check coil resistance | ✔
EC | E-Series | Outdoor Unit | Inlet water temperature abnormal | Water temperature out of operating range (water-cooled systems) | Check water flow rate and temperature; inspect heat exchanger | —
EF | E-Series | Outdoor Unit | Thermal storage unit defect | Thermal storage EEV, PCB or sensor fault | Check thermal storage unit components; inspect EEV and PCB | —
F3 | F-Series | Outdoor Unit | High discharge pipe temperature | Discharge temperature exceeded 110°C; low refrigerant charge; restriction | Check refrigerant charge; inspect EEV; check discharge pipe thermistor | ✔
F6 | F-Series | Outdoor Unit | High pressure in cooling / refrigerant overcharge | Refrigerant overcharged; dirty outdoor coil; outdoor fan issue | Check refrigerant charge; clean condenser; verify fan operation | ✔
H0 | H-Series | Outdoor Unit | Compressor sensor system fault | All compressor-related sensors disconnected simultaneously | Check all sensor connectors on outdoor PCB; re-seat or replace | ✔
H1 | H-Series | Outdoor Unit | Humidifier damper fault | Defective limit switch or damper actuator | Check damper motor and limit switch; replace as needed | —
H3 | H-Series | Outdoor Unit | High pressure switch open circuit | HP switch failed open; wiring fault | Measure continuity of HP switch; replace if failed open | ✔
H4 | H-Series | Outdoor Unit | Low pressure switch open circuit | LP switch failed open; wiring fault | Measure continuity of LP switch; replace if failed open | ✔
H5 | H-Series | Outdoor Unit | Compressor overload sensor failure | Defective compressor overload (OL) sensor | Check OL sensor wiring and resistance; replace if faulty | —
H6 | H-Series | Outdoor Unit | Inverter compressor position sensor failure | Inverter position detection error; inverter PCB or compressor feedback fault | Check inverter board and compressor position feedback wiring | ✔
H7 | H-Series | Outdoor Unit | Outdoor fan motor signal fault | Defective fan motor position sensor or outdoor PCB | Check fan motor and signal wiring to PCB; replace faulty component | ✔
H8 | H-Series | Outdoor Unit | Compressor input current sensor error | Defective power transistor, PCB or reactor | Check inverter PCB current sensing circuit; replace if defective | ✔
H9 | H-Series | Outdoor Sensor | Outdoor ambient temperature sensor fault | Ambient sensor open or short circuit; defective PCB | Measure thermistor resistance; compare to temperature-resistance chart; replace if needed | ✔
J1 | J-Series | Outdoor Sensor | Pressure sensor failure | Pressure transducer failed; defective PCB | Check pressure sensor wiring; replace sensor if out of range | ✔
J2 | J-Series | Outdoor Unit | Current sensor failure | Defective current sensor, PCB or compressor fault | Check current sensor and PCB current sensing circuit | ✔
J3 | J-Series | Outdoor Sensor | Discharge pipe thermistor abnormality | Discharge pipe sensor open or short circuit; connector loose | Measure sensor resistance; replace thermistor or check connector | ✔
J4 | J-Series | Outdoor Sensor | Outdoor coil vapour thermistor fault | Sensor open or short circuit | Measure resistance; replace thermistor | ✔
J5 | J-Series | Outdoor Sensor | Suction pipe thermistor fault | Suction pipe sensor open or short circuit; loose connector | Measure resistance; check connector; replace thermistor if faulty | ✔
J6 | J-Series | Outdoor Sensor | Outdoor heat exchanger thermistor fault | Coil sensor open or short circuit | Measure resistance against temperature chart; replace if out of range | ✔
J7 | J-Series | Outdoor Sensor | Liquid pipe thermistor fault (main) | Liquid pipe sensor open or short circuit | Check sensor connector; replace thermistor | ✔
J8 | J-Series | Outdoor Sensor | Liquid pipe thermistor fault (sub) | Secondary liquid pipe sensor open or short circuit | Check sensor connector; replace thermistor | ✔
J9 | J-Series | Outdoor Sensor | Sub-cool heat exchanger thermistor fault | Sub-cooler sensor open or short circuit | Measure resistance; replace thermistor; check PCB connector | ✔
JA | J-Series | Outdoor Sensor | High pressure transducer failure | HP transducer open or short circuit; wiring fault | Check pressure transducer wiring and output voltage; replace if faulty | ✔
JC | J-Series | Outdoor Sensor | Low pressure transducer failure | LP transducer open or short circuit; wiring fault | Check pressure transducer wiring and output voltage; replace if faulty | ✔
JH | J-Series | Outdoor Sensor | Oil temperature sensor failure | Oil temperature sensor open or short circuit | Check oil temperature sensor wiring; replace if out of range | —
L0 | L-Series | Outdoor/Inverter | Inverter system malfunction | Defective power transistor or inverter PCB; protection activated | Check inverter PCB; replace power transistor or inverter board | —
L1 | L-Series | Outdoor/Inverter | Inverter PCB failure | Blown fuse; defective inverter PCB; failed fan motor | Check inverter fuses; replace inverter PCB if confirmed defective | ✔
L3 | L-Series | Outdoor/Inverter | Electrical box temperature >120°C (comp off) | Defective fan motor; blocked airflow; PCB or power transistor fault | Check electrical box fan; clear blockages; check power transistor | —
L4 | L-Series | Outdoor/Inverter | Inverter heat sink temperature >93°C | Blocked airflow at heat sink; failed temperature sensor; short circuit | Clear airflow path; clean heat sink fins; check fin sensor | ✔
L5 | L-Series | Outdoor/Inverter | Inverter instantaneous DC overcurrent | Defective inverter PCB; compressor winding fault; compressor lock | Check compressor insulation resistance; inspect inverter PCB power section | ✔
L6 | L-Series | Outdoor/Inverter | Inverter instantaneous AC overcurrent | Defective inverter unit; compressor locked or windings shorted | Check compressor windings; replace inverter unit if confirmed | —
L8 | L-Series | Outdoor/Inverter | Inverter compressor overcurrent | Inverter PCB defect; compressor lock or winding fault | Check compressor amp draw; inspect inverter PCB | ✔
L9 | L-Series | Outdoor/Inverter | Inverter compressor start-up failure | Defective inverter PCB; compressor locked or windings; low refrigerant charge | Check refrigerant charge; test compressor; replace inverter PCB if confirmed | ✔
LA | L-Series | Outdoor/Inverter | Power transistor failure | Defective power transistor; PCB fault; compressor issue | Measure transistor; replace if failed; check compressor | —
LC | L-Series | Outdoor/Inverter | Communication failure between main & inverter PCB | Noise; defective inverter PCB; main PCB; fan PCB; noise filter | Check all PCB connectors; replace inverter or main PCB if confirmed defective | ✔
P1 | P-Series | Outdoor Unit | Power supply phase imbalance | Open phase; voltage imbalance between phases; defective main capacitor | Check 3-phase supply voltages; verify main capacitor condition; inspect inverter PCB | ✔
P2 | P-Series | Outdoor Unit | Auto refrigerant charge operation stopped | Closed stop valve; closed refrigerant cylinder valve during auto charge | Check all stop valves are open; verify cylinder valve; restart auto charge | —
P3 | P-Series | Outdoor Unit | Electrical box temperature rise | Defective fin sensor; PCB issue; high ambient temperature | Check fin sensor; inspect PCB; ensure adequate ventilation around unit | ✔
P4 | P-Series | Outdoor Sensor | Radiating fin sensor failure | Fin temperature sensor open or short circuit | Measure fin sensor resistance; replace sensor | ✔
P8 | P-Series | Outdoor Unit | Coil freeze protection during auto charge | Refrigerant cylinder valve closed; insufficient flow | Close refrigerant cylinder and restart auto charge procedure | —
PJ | P-Series | Outdoor Unit | Capacity setting not set or error | Capacity setting adaptor not fitted; incorrect setting | Verify and install correct capacity setting adaptor | ✔
U0 | U-Series | System | Refrigerant shortage detected | System undercharged; EEV fault; faulty pressure or temperature sensor | Check for refrigerant leaks; verify charge; check EEV and sensors | ✔
U1 | U-Series | System | Reversed or missing phase | Reversed phase sequence; missing phase in 3-phase supply | Check phase sequence with meter; verify all 3 phases present and correct | ✔
U2 | U-Series | System | Power supply fault / instantaneous failure | Power supply voltage fault; capacitor wiring error; instantaneous power failure | Check power supply voltage stability; check capacitor wiring; verify earthing | ✔
U3 | U-Series | System | Check operation not executed | Commissioning check operation not performed after installation or PCB replacement | Run check operation from remote controller in test/inspection mode | ✔
U4 | U-Series | System | Communication failure — indoor ↔ outdoor | Wiring fault on F1/F2 transmission wiring; defective PCB; pump wired across comms | Check F1/F2 wiring polarity and continuity; ensure no external devices across terminals | ✔
U5 | U-Series | System | Communication failure — remote ↔ indoor PCB | Wiring fault between remote controller and indoor PCB; defective controller or PCB | Check remote controller wiring and connections; swap controller to test | ✔
U6 | U-Series | System | Communication failure between indoor units | Wiring fault; defective indoor PCB in multi-indoor system | Check inter-indoor unit wiring; isolate faulty unit | ✔
U7 | U-Series | System | Communication failure between outdoor units/PCBs | Defective outdoor PCB; wiring error between outdoor units | Check outdoor-to-outdoor wiring; verify PCB communication boards | ✔
U8 | U-Series | System | Communication failure between remote controllers | Main/sub switch not set correctly; wiring error; defective remote controller | Verify main/sub setting on remote controllers; check wiring | ✔
U9 | U-Series | System | System communication failed | Fault in another indoor unit (e.g. A9); no power to unit; system-wide comms issue | Check all indoor units for individual faults; verify power to all units | ✔
UA | U-Series | System | Improper unit combination / field setting error | Excess indoor units connected; incorrect PCB setting; mismatch of unit capacities | Verify total connected indoor capacity ≤ outdoor capacity; check field settings | ✔
UC | U-Series | System | Duplicated centralised control address | Two or more devices share same address on central control network | Check address settings on all central control devices; assign unique addresses | ✔
UE | U-Series | System | Communication failure — indoor to central control | Wiring error between indoor unit and centralised controller; PCB fault; setting | Check wiring from indoor unit to BMS/central controller; verify address settings | ✔
UF | U-Series | System | Wiring / piping mismatch | Indoor-outdoor wiring error detected; possible PCB defect | Verify F1/F2 wiring is correct indoor to outdoor; run check operation | ✔
UH | U-Series | System | System malfunction | Unaddressed indoor unit; indoor/outdoor unit mismatch; freeze protection active | Check all unit addresses; verify indoor-outdoor compatibility; check for freeze protection | ✔
UJ | U-Series | System | Accessory device communication failure | Defective accessory device (e.g. BS unit, HRV); wiring error to accessory | Check accessory device wiring and power; replace if defective | ✔
M1 | M-Series | Central Control | Central controller PCB failure | Failure of central controller PCB | Check central controller PCB; replace if confirmed defective | ✔
M8 | M-Series | Central Control | Communication failure — central to optional controllers | Communication failed between central controller and optional devices | Check wiring between central controller and optional devices; verify settings | ✔
MA | M-Series | Central Control | Improper combination of optional controllers | Incorrect settings; faulty central controller | Review optional controller combination and address settings | ✔
MC | M-Series | Central Control | Duplicated central controller address | Two or more central controllers share same address | Reassign unique addresses to each central controller | ✔
60 | 6x-Series | HRV / Legacy | Overall alarm | Open circuit across J1-JC terminals | Check wiring at J1-JC terminals; inspect for open circuit | —
64 | 6x-Series | HRV / Legacy | Return air sensor failure | Return air sensor open or short circuit | Check sensor and wiring; replace if faulty | —
65 | 6x-Series | HRV / Legacy | Ambient sensor failure | Ambient temperature sensor open or short circuit | Check sensor and wiring; replace if faulty | —
6A | 6x-Series | HRV / Legacy | Damper system failure | Defective damper motor, limit switch or PCB | Check damper motor, limit switch and PCB; replace faulty component | —

## Quick Lookup
DAIKIN ERROR CODE — QUICK LOOKUP
FSXQ-A Indoor ¦ RXYTQ Outdoor ¦ BRC1H81W Madoka Controller
Code | Series / Location | Definition (Short) | Top Cause | VRV?
60 | 6x-Series / HRV / Legacy | Overall alarm | Open circuit across J1-JC terminals | —
64 | 6x-Series / HRV / Legacy | Return air sensor failure | Return air sensor open or short circuit | —
65 | 6x-Series / HRV / Legacy | Ambient sensor failure | Ambient temperature sensor open or short circuit | —
6A | 6x-Series / HRV / Legacy | Damper system failure | Defective damper motor, limit switch or PCB | —
A0 | A-Series / Indoor Unit | External protection device active | External protection wired to T1-T2 terminals is active | ✔
A1 | A-Series / Indoor Unit | Indoor PCB failure | Defective PCB or electrical noise interference | ✔
A3 | A-Series / Indoor Unit | High water level / drain fault | Float switch open circuit | ✔
A5 | A-Series / Indoor Unit | Freeze-up / high pressure protection | Poor airflow, short circuit, EEV fault, low refrigerant, bad coil thermistor | ✔
A6 | A-Series / Indoor Unit | Indoor fan motor failure | Locked rotor, overcurrent, overload, broken wiring or bad connector | ✔
A7 | A-Series / Indoor Unit | Louvre / swing flap motor failure | Defective louvre motor, indoor PCB, or connecting cable | ✔
A8 | A-Series / Indoor Unit | Power supply / AC input overcurrent | Defective power supply voltage | —
A9 | A-Series / Indoor Unit | Electronic Expansion Valve (EEV) failure | Defective EEV motor coil, indoor PCB, or relay cable | ✔
AA | A-Series / Indoor Unit | Heater overheat | Auxiliary heater overtemperature | —
AF | A-Series / Indoor Unit | High water level (thermo-off condition) | Float switch open circuit while thermostat is OFF | ✔
AH | A-Series / Indoor Unit | Air filter / dust collector malfunction | Defective dust collecting element | ✔
AJ | A-Series / Indoor Unit | Capacity setting error | Capacity setting adaptor not installed or incorrect adaptor fitted | ✔
C1 | C-Series / Indoor Unit | Communication failure — main to sub PCB | Failed communication between main PCB and fan motor control driver sub-PCB | ✔
C4 | C-Series / Indoor Sensor | Indoor coil thermistor fault (liquid pipe) | Open or short circuit in liquid pipe thermistor | ✔
C5 | C-Series / Indoor Sensor | Suction / gas pipe thermistor fault | Open or short circuit in suction pipe thermistor | ✔
C6 | C-Series / Indoor Unit | Fan motor sensor / driver failure | Defective fan PCB or capacity setting adaptor | ✔
C7 | C-Series / Indoor Sensor | Front panel / louver position sensor fault | Defective limit switch or front panel driving motor | —
C9 | C-Series / Indoor Sensor | Return air temperature thermistor fault | Return air sensor open or short circuit | ✔
CA | C-Series / Indoor Sensor | Discharge air thermistor fault | Discharge air sensor open or short circuit | ✔
CC | C-Series / Indoor Sensor | Humidity sensor failure | Failed humidity sensor in unit | —
CJ | C-Series / Indoor Sensor | Remote temperature sensor failure | Defective remote controller sensor | ✔
E0 | E-Series / Outdoor Unit | Outdoor protection device tripped | Outdoor unit safety device (thermal, pressure) activated | ✔
E1 | E-Series / Outdoor Unit | Outdoor PCB failure | Defective outdoor main PCB or electrical noise | ✔
E3 | E-Series / Outdoor Unit | High pressure switch tripped | Dirty condenser coil | ✔
E4 | E-Series / Outdoor Unit | Low pressure switch tripped | Refrigerant leak | ✔
E5 | E-Series / Outdoor Unit | Inverter compressor locked / overheated | Compressor mechanically locked | ✔
E6 | E-Series / Outdoor Unit | Fan motor locked / high current (DOL) | Fan motor stuck | ✔
E7 | E-Series / Outdoor Unit | Outdoor fan motor failure | Defective fan motor or outdoor PCB | ✔
E8 | E-Series / Outdoor Unit | Inverter compressor high current | Compressor drawing excessive current | ✔
E9 | E-Series / Outdoor Unit | Outdoor EEV motor failure | Defective EEV motor or outdoor PCB | ✔
EA | E-Series / Outdoor Unit | 4-way valve abnormality | Defective reversing valve solenoid, PCB, or associated sensor | ✔
EC | E-Series / Outdoor Unit | Inlet water temperature abnormal | Water temperature out of operating range (water-cooled systems) | —
EF | E-Series / Outdoor Unit | Thermal storage unit defect | Thermal storage EEV, PCB or sensor fault | —
F3 | F-Series / Outdoor Unit | High discharge pipe temperature | Discharge temperature exceeded 110°C | ✔
F6 | F-Series / Outdoor Unit | High pressure in cooling / refrigerant overcharge | Refrigerant overcharged | ✔
H0 | H-Series / Outdoor Unit | Compressor sensor system fault | All compressor-related sensors disconnected simultaneously | ✔
H1 | H-Series / Outdoor Unit | Humidifier damper fault | Defective limit switch or damper actuator | —
H3 | H-Series / Outdoor Unit | High pressure switch open circuit | HP switch failed open | ✔
H4 | H-Series / Outdoor Unit | Low pressure switch open circuit | LP switch failed open | ✔
H5 | H-Series / Outdoor Unit | Compressor overload sensor failure | Defective compressor overload (OL) sensor | —
H6 | H-Series / Outdoor Unit | Inverter compressor position sensor failure | Inverter position detection error | ✔
H7 | H-Series / Outdoor Unit | Outdoor fan motor signal fault | Defective fan motor position sensor or outdoor PCB | ✔
H8 | H-Series / Outdoor Unit | Compressor input current sensor error | Defective power transistor, PCB or reactor | ✔
H9 | H-Series / Outdoor Sensor | Outdoor ambient temperature sensor fault | Ambient sensor open or short circuit | ✔
J1 | J-Series / Outdoor Sensor | Pressure sensor failure | Pressure transducer failed | ✔
J2 | J-Series / Outdoor Unit | Current sensor failure | Defective current sensor, PCB or compressor fault | ✔
J3 | J-Series / Outdoor Sensor | Discharge pipe thermistor abnormality | Discharge pipe sensor open or short circuit | ✔
J4 | J-Series / Outdoor Sensor | Outdoor coil vapour thermistor fault | Sensor open or short circuit | ✔
J5 | J-Series / Outdoor Sensor | Suction pipe thermistor fault | Suction pipe sensor open or short circuit | ✔
J6 | J-Series / Outdoor Sensor | Outdoor heat exchanger thermistor fault | Coil sensor open or short circuit | ✔
J7 | J-Series / Outdoor Sensor | Liquid pipe thermistor fault (main) | Liquid pipe sensor open or short circuit | ✔
J8 | J-Series / Outdoor Sensor | Liquid pipe thermistor fault (sub) | Secondary liquid pipe sensor open or short circuit | ✔
J9 | J-Series / Outdoor Sensor | Sub-cool heat exchanger thermistor fault | Sub-cooler sensor open or short circuit | ✔
JA | J-Series / Outdoor Sensor | High pressure transducer failure | HP transducer open or short circuit | ✔
JC | J-Series / Outdoor Sensor | Low pressure transducer failure | LP transducer open or short circuit | ✔
JH | J-Series / Outdoor Sensor | Oil temperature sensor failure | Oil temperature sensor open or short circuit | —
L0 | L-Series / Outdoor/Inverter | Inverter system malfunction | Defective power transistor or inverter PCB | —
L1 | L-Series / Outdoor/Inverter | Inverter PCB failure | Blown fuse | ✔
L3 | L-Series / Outdoor/Inverter | Electrical box temperature >120°C (comp off) | Defective fan motor | —
L4 | L-Series / Outdoor/Inverter | Inverter heat sink temperature >93°C | Blocked airflow at heat sink | ✔
L5 | L-Series / Outdoor/Inverter | Inverter instantaneous DC overcurrent | Defective inverter PCB | ✔
L6 | L-Series / Outdoor/Inverter | Inverter instantaneous AC overcurrent | Defective inverter unit | —
L8 | L-Series / Outdoor/Inverter | Inverter compressor overcurrent | Inverter PCB defect | ✔
L9 | L-Series / Outdoor/Inverter | Inverter compressor start-up failure | Defective inverter PCB | ✔
LA | L-Series / Outdoor/Inverter | Power transistor failure | Defective power transistor | —
LC | L-Series / Outdoor/Inverter | Communication failure between main & inverter PCB | Noise | ✔
M1 | M-Series / Central Control | Central controller PCB failure | Failure of central controller PCB | ✔
M8 | M-Series / Central Control | Communication failure — central to optional controllers | Communication failed between central controller and optional devices | ✔
MA | M-Series / Central Control | Improper combination of optional controllers | Incorrect settings | ✔
MC | M-Series / Central Control | Duplicated central controller address | Two or more central controllers share same address | ✔
P1 | P-Series / Outdoor Unit | Power supply phase imbalance | Open phase | ✔
P2 | P-Series / Outdoor Unit | Auto refrigerant charge operation stopped | Closed stop valve | —
P3 | P-Series / Outdoor Unit | Electrical box temperature rise | Defective fin sensor | ✔
P4 | P-Series / Outdoor Sensor | Radiating fin sensor failure | Fin temperature sensor open or short circuit | ✔
P8 | P-Series / Outdoor Unit | Coil freeze protection during auto charge | Refrigerant cylinder valve closed | —
PJ | P-Series / Outdoor Unit | Capacity setting not set or error | Capacity setting adaptor not fitted | ✔
U0 | U-Series / System | Refrigerant shortage detected | System undercharged | ✔
U1 | U-Series / System | Reversed or missing phase | Reversed phase sequence | ✔
U2 | U-Series / System | Power supply fault / instantaneous failure | Power supply voltage fault | ✔
U3 | U-Series / System | Check operation not executed | Commissioning check operation not performed after installation or PCB replacement | ✔
U4 | U-Series / System | Communication failure — indoor ↔ outdoor | Wiring fault on F1/F2 transmission wiring | ✔
U5 | U-Series / System | Communication failure — remote ↔ indoor PCB | Wiring fault between remote controller and indoor PCB | ✔
U6 | U-Series / System | Communication failure between indoor units | Wiring fault | ✔
U7 | U-Series / System | Communication failure between outdoor units/PCBs | Defective outdoor PCB | ✔
U8 | U-Series / System | Communication failure between remote controllers | Main/sub switch not set correctly | ✔
U9 | U-Series / System | System communication failed | Fault in another indoor unit (e.g. A9) | ✔
UA | U-Series / System | Improper unit combination / field setting error | Excess indoor units connected | ✔
UC | U-Series / System | Duplicated centralised control address | Two or more devices share same address on central control network | ✔
UE | U-Series / System | Communication failure — indoor to central control | Wiring error between indoor unit and centralised controller | ✔
UF | U-Series / System | Wiring / piping mismatch | Indoor-outdoor wiring error detected | ✔
UH | U-Series / System | System malfunction | Unaddressed indoor unit | ✔
UJ | U-Series / System | Accessory device communication failure | Defective accessory device (e.g. BS unit, HRV) | ✔